RFP 23-03		 September 16, 2022
Bid Form

ADDENDUM NO. 2

BID NO.  23-03
CRESTMONT SEWER REPLACEMENT
HILLCREST MANOR UTL-16-10

To all holders of the specifications, the following corrections are hereby made.  All other items shall remain unchanged. This addendum shall become part of the Contract Documents for the above referenced project. 

Acknowledgement of Addendum

Name: ___________________________________________________

Company: ________________________________________________

Date: ____________________________________________________

Signature: ________________________________________________


· Section 1: Answers to Questions Posed During Pre-Bid Meeting:

Q1: Will an Engineer’s Estimate be provided? 
A1:  The City is not providing an Engineer’s Estimate, the amount that has been allocated for this project is $300,000	
Q2: On the topic of sewer activity and bypassing:
A2:  To clarify, the existing sewer must remain active as the new sewer is installed.  Contractor is responsible for bypassing and reinstating service each day.
Q3: On the topic of existing and proposed locations as shown on the drawings:
A3:  The new pipe and manholes should be installed in place of the existing sewer, only deviating where it is necessary to maintain a straight path between manholes.  New pipe should not be deflected or elbowed.  All angles and changes in direction must be located in manholes as shown.
Q4: On the topic of optional service relocation at 214 Hemlock:
A4:  The entire scope of the project shall be covered under the lump sum, except the optional relocation of the service to 214 Hemlock.  The service relocation should be broken out as a separate optional cost.  The City will announce whether or not this part of the project when the bid is awarded.
Q5: Where is the staging area?	
A5: Equipment and material staging will be assigned an area on Laurel Lane. (about 475ft NE of Crestmont site.)


Q6: On the topic of visual depiction of sewer and storm on drawings:
A6: The visual separation of the sewer lines and storm drain lines is exaggerated to make the plans easier to read.  Parallel lines may be closer to or further away from one another than depicted on the drawings.
Q7: On the topic of stormwater locations and configuration:
A7: The morning of 9-16-22, we field verified (using tracer dye and radio location) that the storm drain lines are configured as shown on the project drawings.   The storm lines are shallower than the sewer and do cross over at some points.  For the most part the storm drains are 3-4 ft away (laterally) from the sewer running parallel.  The contractor is responsible for verifying locations of conflicting utilities and stabilizing/protecting any exposed lines.
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