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Bid Form

ADDENDUM NO. 3

BID NO.  23-03
CRESTMONT SEWER REPLACEMENT
HILLCREST MANOR UTL-16-10

To all holders of the specifications, the following corrections are hereby made.  All other items shall remain unchanged. This addendum shall become part of the Contract Documents for the above referenced project. 

Acknowledgement of Addendum

Name: ___________________________________________________

Company: ________________________________________________

Date: ____________________________________________________

Signature: ________________________________________________




Q1: Are the existing service laterals to each house in the same location as the proposed? 
A1:  The proposed service laterals depicted on the prints are shown in the approximate locations of the existing service laterals.  The new laterals are to be installed in place of the old, removing existing material and replacing as specified.  Camera inspections were used to measure tap locations for each service and those measurements were used to approximate the service locations on the plans.



Q2: How is the existing sewer line to be abandoned (i.e. is it to be filled with concrete)? 
A2:  The new pipe and manholes should be installed in place of the existing sewer, only deviating where it is necessary to maintain a straight path between manholes.  New pipe should not be deflected or elbowed.  All angles and changes in direction must be located in manholes as shown.  When installing new pipe in place of existing, the old material should be removed.  In the instances where the new pipe deviates from the path of the existing, the old pipe should be filled, plugged or capped as necessary to prevent voids and sinkholes from forming in the future.



Q3: The Special Provisions call for milling and overlay of the Crestmont Dr and Hemlock Dr. How deep is the surface to be milled and what type of mix is to be used to replace it? What are the limits of milling and paving along Hemlock Ln? The special provisions only mention “parts” of it. 
A3:  Crestmont Dr will be entirely resurfaced per Harford County Detail Plate R-4 in the project drawings.  All excavated areas will be backfilled with compacted crushed stone to limit on utility bedding details, then paved with 6” of base hot mix.  (see plate R-4).  The entirety of the area of Crestmont Dr should be milled and overlayed with 3” of surface hot mix.  The areas that extend outside of Crestmont drive should also be paved per detail R-4 but only the area that was excavated.  Base layer at 6” thick and surface layer at 3” extending 3’ in each direction from excavation.  See red shaded areas in drawing below for general idea:
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