RFP 23-06		 November 15, 2022
Addendum No 1

ADDENDUM NO. 2

BID NO.  23-06
FESTIVAL PARK ELECTRICAL IMPROVEMENTS

To all holders of the specifications, the following corrections are hereby made.  All other items shall remain unchanged. This addendum shall become part of the Contract Documents for the above referenced project. 

Acknowledgement of Addendum

Name: ___________________________________________________

Company: ________________________________________________

Date: ____________________________________________________

Signature: ________________________________________________

Q1) During pre-bid meeting, on Nov 10, 2022, Contractors discussed whether or not the City would allow the re-use of existing pedestals, conduit and handholes or require new.  
  
A1)  The following configuration would be acceptable to the City, however, the contractor shall be governed by the NEC, when pulling the permit for this work. 

	a. At the circuit panel an additional contactor (match the existing), may be added for a second phase to be placed in the exiting conduit.
	b. The existing conduit and handhole network may be used for the additional phase to each pedestal location. 
	c. At the existing pedestal and conduit, a new outlet box may be added to replace the existing box for both circuits.  If this is proposed by the contractor, contractor may use a Midwest U011C010 box or equivalent.  The new enclosure shall contain a breaker and outlet for each circuit.  The existing inline fuse at each handhole shall be removed.
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MIDWEST U011C010 70A SURFACE UNMETERED 20GFCI/20GFCI

Description:

MIDWEST U011C010 70A SURFACE UNMETERED 20GFCI/20GFCI

Technical Description:

Unmetered Type; G90 Galvanized Steel Material; Zinc Coated
Finish

UPC: 78456756721

Part Number: U011C010




