RFP 23-03		 October 4, 2022
Addendum No 1

ADDENDUM NO. 1

BID NO.  23-02
[bookmark: _Hlk115791759]ELEVATOR MODERNIZATION 
CITY HALL BUILDING

To all holders of the specifications, the following corrections are hereby made.  All other items shall remain unchanged. This addendum shall become part of the Contract Documents for the above referenced project. 

Acknowledgement of Addendum

Name: ___________________________________________________

Company: ________________________________________________

Date: ____________________________________________________

Signature: ________________________________________________

Q1) Approximately when will be the anticipated NTP?
A1) See Bid Form Para 2: This Bid will remain subject to acceptance for a period of 60 days from the date of Bid opening unless award is delayed by a required approval from a governmental agency, the sale of bonds, or the award of a grant or grants, in which event the Bids shall remain open for a period of 120 days from the date of Bid opening. Thirty-day (30) Calendar extensions of the date for the award may be made by the mutual written consent of the City and the apparent Successful Bidder. Under normal practices, the City anticipates review and recommendation of the successful bid to council within 30 days of bid opening.   

Q2) Is full time on-site supervision required from the prime contractor or will it be acceptable for the elevator contractor’s foreman to act as the supervisor when only elevator-specific work is taking place?
A2) The City requires a single point to provide supervision of contact from the prime contractor.  The City is not responsible for managing sub-contractors.  The prime may designate an alternate however, this does not relieve the prime in meeting all contract obligations.      

Q3) Please confirm that this project will be subject to prevailing wage law requirements if the final contract sum is above $250,000. Please provide the prevailing wage rates to be used for bidding purposes if they will be required.
A3) This project is not subject to prevailing wage law requirements



Q4) Will a building permit be required by the GC? If so, will the City cover the fees? 
A4) All applicable permits will be obtained by the GC.  The GC needs to factor any fees by Harford County into the bid amount.

Q5) Will a staging area be provided to the contractor within the facility?
A5) Space is limited on-site.  The Contractor will need to state space requirements for staging before work commences.  If the Contractor needs to utilize an outdoor storage container or ‘pod’, the City can accommodate space in the parking lot for one or two parking spaces on-site.

Q6) Will the contractor be provided access to use the bathrooms at the facility? 
A6) Public bathroom facilities are available on-site.

Q7) Will the contractor be provided free parking at the facility?
A7) There is a limited amount of parking spaces for employees, therefore, the contractor can use any parking spaces along the front of City Hall for their workers. There are no fees for parking on public roads.  

Q8) Please provide the contact information for the incumbent fire alarm contractor/server. 
A8) The fire alarm contractor is Johnson Controls out of Baltimore, MD.  Specific contact details will be provided to successful bidder before work commences.

Q9) Is painting of the machine room floor, ceiling, and walls a requirement for this project?
A9) This project requires painting of the floors only, unless there is damage to other areas from modernization that require repair and painting.

Q10) Spec Section 1.2 – Please confirm an acceptable location for the outdoor condenser unit and provide an approximate run length from the elevator machine room.  
A10) The outdoor condenser unit should be mounted to the wall closest to the elevator, just outside the machine room and stairwell, at the rear of the building and in way that does not impede pedestrian access.  The exact location and configuration will be confirmed with the successful bidder.

Q10-a) If the rooftop must be utilized: please confirm whether the roof is under warranty and if so provide the contact information for the warranty holder.  
	A10-a) The rooftop will not be utilized for the outdoor condenser. 

Q10-b) Will a cage be required at the outdoor condenser location for security?  
A10-b) A security cage will not be required.



Q10-c) Confirm the existing machine room HVAC is to be demolished and removed. 
A10-c) There is no existing HVAC in elevator machine room to be removed.

Q11) Spec Section 1.6 – Please confirm this work is required as a part of the contract. 
A11) Yes this work is part of the contract.

Q12) Please confirm an elevator sump pump is required as a part of the contract.
A12) Yes sump pump is required.

Q13) The pit was observed to be wet / dirty at the site visit. Please confirm if elevator pit cleaning and application of damp-proofing sealant will be required as a part of the contract.
A13) Yes the pit will need to be sealed as well as painted.

Q14) Spec Section 2.6.1 – This section mentions that the contractor shall provide an allowance for the refurbishment of the cab interior. Other parts of the specification outline a scope to refurbish the cab interior. Please clarify the dollar amount the contractor should include within their base bid price to refurbish the elevator cab interior.
A14) The allowance should cover the costs of a standard cab with colors and finishes chosen by ownership.

Q15) There is existing sprinkler piping located at the top of the elevator shaft, which DLLR may interpreted as being above the elevator equipment. Please confirm the contractor is required to relocate this piping.
A15) All that is required are heat and smoke devices at top of hoist-way as well as shunt-trip added to mainline circuit, both as required by code.

Q16) The lobby lighting at the main lobby landing does not appear to meet code requirements. Please confirm that new elevator lobby lighting is required as a part of this contract.
A16) If the existing lobby lighting does not meet the minimum 10fc lumens required by code then it must be corrected as a part of this contract.

Q17) Please confirm that the elevator machine room door and frame can be retained in place.
A17) If the existing door and frame meet UL rating requirements they can be retained.
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